EcoWell MQTT-Modbus Gateway

Architecture & Design Document

Platform: ESP32-S3 (Freenove ESP32-S3-WROOM)
Framework: Arduino + FreeRTOS
Build System: PlatformIO

# 1. Project Overview

This firmware implements an Industrial IoT Gateway for an EcoWell water softener system. It bridges Modbus RTU field sensors/actuators to an MQTT cloud broker over Wi-Fi, enabling remote monitoring, telemetry, alerting, and command execution.

## What It Does

| Capability | Description |
| --- | --- |
| Sensor Polling | Periodically reads water flow, pressure, salt level, TDS, power status, and regeneration status from Modbus slave devices |
| Cloud Telemetry | Publishes sensor data as structured JSON to an MQTT broker at configurable intervals |
| Remote Commands | Receives cloud commands (e.g., trigger regeneration) via MQTT subscriptions and writes to Modbus actuators |
| Business Logic | Runs a water softener state machine — detects faults (low pressure, low salt), manages regeneration cycles |
| Alerting | Translates system events (faults, regen lifecycle) into severity-tagged JSON alerts published to a dedicated MQTT topic |
| Auto-Recovery | Wi-Fi auto-reconnect, MQTT reconnect, and Modbus communication health tracking |

## Technology Stack

| Layer | Technology |
| --- | --- |
| Microcontroller | ESP32-S3 (Dual-core Xtensa LX7, 240 MHz) |
| Framework | Arduino (via PlatformIO) |
| RTOS | FreeRTOS (bundled with ESP-IDF/Arduino) |
| Modbus Library | eModbus — Modbus RTU Client |
| MQTT Library | PsychicMqttClient — Async MQTT |
| JSON Library | ArduinoJson v7 — Serialization/Deserialization |
| Build System | PlatformIO |

# 2. High-Level Architecture

The system follows a layered, event-driven architecture with clear separation of concerns. Each module has its own FreeRTOS task and communicates via queues and events.

Figure: Architecture Diagram

# 3. Module Breakdown

## 3.1  Foundation Layer

These modules provide infrastructure that every other module depends on.

logger — logger.h / logger.cpp

Thread-safe serial logger using a FreeRTOS mutex. Provides four severity macros (LOG_INFO, LOG_WARN, LOG_ERROR, LOG_DEBUG) that format output as [LEVEL] [MODULE] message.

system_err — system_err.h

Defines the universal return type sys_status_t used by all modules: SYS_OK, SYS_ERR_FAIL, SYS_ERR_TIMEOUT, SYS_ERR_NO_MEMORY, etc.

event_service — event_service.h / event_service.cpp

Facade over the ESP-IDF default event loop. Provides event_register(), event_post(), event_unregister() — enabling fully decoupled publish/subscribe IPC between modules.

system_events — system_events.h / system_events.cpp

Defines two event bases and all event IDs:

| Event Base | Events |
| --- | --- |
| APP_EVENTS | NETWORK_UP, NETWORK_DOWN, MQTT_CONNECTED, MQTT_DISCONNECTED, MODBUS_NETWORK_UP, MODBUS_NETWORK_DOWN, SYSTEM_FAULT |
| CORE_EVENTS | FAULT_LOW_PRESSURE, FAULT_LOW_SALT, FAULT_DATA_LOSS, REGEN_STARTED, REGEN_COMPLETED, REGEN_FAILED |

## 3.2  Data Model Layer

A two-tier data model separates static configuration from live runtime state.

tag_registry — tag_registry.h / tag_registry.cpp

The static data dictionary — a compile-time table of 8 tag definitions. Each tag_config_t stores: identity (tagId, name, unit, topic, topicType), protocol info (source, access, dataType), and Modbus config (slaveId, address, quantity, functionCode, wordOrder).

Tags configured in this system:

| ID | Name | Data Type | Source | MQTT Topic | Access |
| --- | --- | --- | --- | --- | --- |
| 1 | water_flow | FLOAT32 | Modbus | ECO/WS-1/FT-101 | Read |
| 2 | water_pressure | FLOAT32 | Modbus | ECO/WS-1/PT-101 (P: pressure T: transmit) | Read |
| 3 | salt_level | FLOAT32 | Modbus | ECO/WS-1/SALT/AT-101 (A: Analytic T: Transmit) | Read |
| 4 | tds | UINT16 | Modbus | ECO/WS-1/TDS/AT-101 (A: Analytic T: Transmit) | Read |
| 5 | power_status | BOOL | Modbus | ECO/WS-1/YT-101 (Y: Power T: Transmit) | Read |
| 6 | regen_status | BOOL | Modbus | ECO/WS-1/REGEN_STATE | Read |
| 7 | cmd_regen | BOOL | Modbus | ECO/WS-1/CMD_REGEN | Write |
| 8 | core_state | STRING | System | ECO/WS-1/CORE_STATE | Read |

tag_runtime — tag_runtime.h / tag_runtime.cpp

The live value cache — a dynamically allocated array of tag_runtime_t structs (one per tag). Each entry holds: value (tag_value_t union supporting bool, uint16, int16, uint32, int32, float32, string), valid (whether the last read was successful), changed (flag for change-detection), and timestamp (last update time). Thread-safe access via FreeRTOS mutex.

## 3.3  Protocol Layer

modbus_codec — modbus_codec.h / modbus_codec.cpp

Pure utility functions for converting between Modbus uint16_t register arrays and typed tag_value_t values. Supports configurable word order (ABCD, CDAB, BADC, DCBA) for 32-bit types. Uses union-based type punning for IEEE 754 float encoding.

modbus_service — modbus_service.h / modbus_service.cpp

Manages the Modbus RTU master over Serial1 (UART). Configures serial port (19200 baud, 8N2, TX=GPIO17, RX=GPIO18). Dispatches read requests (FC 0x02 for discrete inputs, FC 0x03 for holding registers) and write requests (FC 0x05 for single coil, FC 0x06 for single register, FC 0x10 for multiple registers). Async callbacks decode responses via modbus_codec and post results back to acquisition. Tracks communication health — fires MODBUS_NETWORK_UP / MODBUS_NETWORK_DOWN events.

protocol_dispatcher — protocol_dispatcher.h / protocol_dispatcher.cpp

A routing layer that decouples the acquisition engine from specific protocols. Receives generic protocol_request_t messages from a FreeRTOS queue and routes them based on the tag's source field:

| Tag Source | Routed To |
| --- | --- |
| TAG_SOURCE_MODBUS | modbus_read_request() / modbus_write_request() |
| TAG_SOURCE_SYSTEM | system_service_read_request() |
| TAG_SOURCE_CAN | Placeholder (logged, not yet implemented) |

system_service — system_service.h / system_service.cpp

Handles read requests for internal "system" tags. Currently serves the core_state tag — reads the water softener state machine's current state and returns it as a UINT16 or STRING value.

## 3.4  Connectivity Layer

wifi_service — wifi_service.h / wifi_service.cpp

The largest module (297 lines). Implements a finite state machine for Wi-Fi connection lifecycle:

Figure: Wifi Fsm Diagram

Dedicated FreeRTOS task processes events from a queue. Auto-reconnect with configurable timeout (20s). Arduino WiFi event callbacks translated to internal events.

mqtt_service — mqtt_service.h / mqtt_service.cpp

MQTT client wrapper with: thread-safe publish via FreeRTOS TX queue (producer-consumer pattern), Last Will & Testament (ECO/WS-1/MQTT-STATUS → "offline", QoS 1, retain), auto-reconnect, and state machine (DEINITIALIZED → INITIALIZED → CONNECTING → RUNNING → STOPPED). Inbound messages forwarded to subscriber_post().

## 3.5  Application Layer

acquisition — acquisition.h / acquisition.cpp

The cyclic scan engine. A FreeRTOS task that every 10 seconds iterates all readable tags, builds a protocol_request_t (OP_READ) for each, posts to the protocol dispatcher queue, receives protocol_response_t results on a response queue (capacity: 30), and updates tag_runtime with new values, validity, and timestamps. Pinned to Core 1, priority 5.

publisher — publisher.h / publisher.cpp

A FreeRTOS task that every 20 seconds iterates all tags with TAG_TOPIC_TYPE_PUBLISH, skips invalid tags, serializes each as JSON ({id, ts, type: "telemetry", value}), and publishes to the tag's configured MQTT topic (QoS 1).

subscriber — subscriber.h / subscriber.cpp

Handles inbound MQTT commands. On start, subscribes to all tags with TAG_TOPIC_TYPE_SUBSCRIBE. Receives messages via subscriber_post() (called from MQTT service), looks up tag by topic, validates access mode, deserializes JSON, extracts value. Special case: cmd_regen tag routes to core_request_regen() / core_abort_regen(). General case: builds protocol_request_t (OP_WRITE) and posts to protocol dispatcher.

alert_service — alert_service.h / alert_service.cpp

Subscribes to APP_EVENTS and CORE_EVENTS via the event service, translates them into severity-tagged alerts, and publishes as JSON to ECO/WS-1/ALERTS:

| Event | Severity |
| --- | --- |
| FAULT_LOW_PRESSURE | CRITICAL |
| FAULT_LOW_SALT | CRITICAL |
| REGEN_FAILED | CRITICAL |
| SYSTEM_FAULT | CRITICAL |
| FAULT_DATA_LOSS | WARNING |
| REGEN_STARTED | INFO |
| REGEN_COMPLETED | INFO |

core — core.h / core.cpp

The domain logic brain — a FreeRTOS task evaluating the water softener state machine every 2 seconds:

Figure: Core Fsm Diagram

Reads pressure (tag 2), salt (tag 3), and regen_status (tag 6) from tag_runtime. Fault thresholds: pressure < 20 psi, salt < 10%. Regeneration cycle timeout: 2 minutes.

Remote Command Processing & Safety Interlocks:

Remote command requests (start/abort regeneration) are received via the MQTT subscriber, which calls thread-safe functions (core_request_regen() and core_abort_regen()) to set pending flags protected by a mutex. The core task evaluates these flags at the end of its 2-second loop:

Figure: Safety Checks Flow

Regeneration Stop & Timeout Lifecycle:

A running regeneration cycle can be stopped in three ways: cycle timeout (automatic), remote abort command, or external hardware/manual intervention.

Figure: Regen Stop Flow

## 3.6  Entry Point — main.cpp

The Mediator/Orchestrator. Defines all hardware configuration structs (WiFi, MQTT, Modbus, acquisition, publisher). Calls app_init() — sequential initialization of all 12 modules in dependency order. Calls app_start() — starts alert, core, protocol_dispatcher, acquisition, wifi. Registers an app_event_handler() that coordinates service lifecycle via events:

NETWORK_UP → start MQTT

NETWORK_DOWN → stop MQTT

MQTT_CONNECTED → start publisher & subscriber

MQTT_DISCONNECTED → stop publisher & subscriber

fault_handler() handles critical errors (SYS_ERR_NO_MEMORY triggers reboot). loop() is intentionally empty — all work runs in FreeRTOS tasks.

# 4. Data Flow

## 4.1  Sensor Data (Field → Cloud)

Modbus Slave Devices
    │  RS-485 / Modbus RTU (FC 0x02, 0x03)
    ▼
modbus_service        ← async read request from protocol_dispatcher
    │  raw uint16_t registers
    ▼
modbus_codec          ← decodes to typed tag_value_t (handles word order)
    │  protocol_response_t (tagId + value + status)
    ▼
acquisition           ← posts response to acquisition queue
    │  updates value, valid, changed, timestamp
    ▼
tag_runtime           ← shared in-memory cache (mutex-protected)
    │  reads valid + publishable tags
    ▼
publisher             ← serializes to JSON with ArduinoJson
    │  mqtt_msg_t → TX queue
    ▼
mqtt_service          ← publishes to MQTT broker
    │
    ▼
MQTT Broker (Cloud)

## 4.2  Commands (Cloud → Field)

MQTT Broker (Cloud)
    │  incoming message on subscribed topic
    ▼
mqtt_service          ← onMessage callback
    │  mqtt_msg_t → subscriber queue
    ▼
subscriber            ← finds tag by topic, parses JSON
    │
    ├── cmd_regen? ──► core_request_regen() / core_abort_regen()
    │
    └── general write ──► protocol_request_t (OP_WRITE)
                              │
                              ▼
                    protocol_dispatcher → modbus_write_request()
                              │
                              ▼
                    modbus_service → Modbus RTU slave

## 4.3  Event-Driven Lifecycle

WiFi connects → APP_EVENT_NETWORK_UP → main starts MQTT

MQTT connects → APP_EVENT_MQTT_CONNECTED → main starts publisher + subscriber

MQTT disconnects → APP_EVENT_MQTT_DISCONNECTED → main stops publisher + subscriber

WiFi disconnects → APP_EVENT_NETWORK_DOWN → main stops MQTT

Core detects fault → CORE_EVENT_FAULT_* → alert_service publishes alert JSON

# 5. Concurrency Model

All real work happens in FreeRTOS tasks communicating via queues and events. The Arduino loop() is intentionally empty.

| Task | Core | Priority | Purpose |
| --- | --- | --- | --- |
| acquisitionTask | 1 | 5 | Cyclic scan of all tags (10s interval) |
| protocolDispatcherTask | 1 | 5 | Routes protocol requests to services |
| publisherTask | 1 | 5 | Publishes telemetry to MQTT (20s interval) |
| subscriberTask | 1 | 5 | Processes inbound MQTT commands |
| alertTask | 1 | 5 | Translates events to alert JSON, publishes |
| coreTask | 1 | 5 | Evaluates state machine (2s interval) |
| wifiFSTMTask | 1 | 5 | Wi-Fi connection FSM |
| mqttTask | 1 | 5 | Dequeues and sends MQTT messages |

Synchronization Mechanisms:

FreeRTOS Queues — acquisition responses (30-deep), protocol requests, MQTT TX, subscriber inbox, alert inbox, WiFi events

FreeRTOS Mutex — tag_runtime access, Modbus bus lock, logger serial output

portMUX Spinlock — core state access, MQTT state access, WiFi connection state

# 6. Design Patterns

| Pattern | Where | Why |
| --- | --- | --- |
| Event-Driven Architecture | Entire system | Modules are decoupled; lifecycle is coordinated via events rather than direct calls |
| Mediator | main.cpp | Centralizes all module coordination and lifecycle orchestration |
| Finite State Machine | core.cpp, wifi_service.cpp | Manages complex state transitions with well-defined states and transitions |
| Producer-Consumer | All FreeRTOS queues | Thread-safe asynchronous communication between tasks |
| Strategy / Router | protocol_dispatcher.cpp | Routes requests to different protocol handlers based on tag source |
| Registry | tag_registry.cpp | Central lookup table for tag configuration |
| Facade | event_service.cpp | Simplifies the ESP-IDF event loop API |
| Codec | modbus_codec.cpp | Isolates serialization / byte-order concerns from business logic |
| Observer | alert_service.cpp | Subscribes to events and reacts to state changes |
| Service Lifecycle | All modules | Consistent init() → start() → stop() pattern with state enums |

# 7. Module Dependency Graph

main.cpp (orchestrator)
  ├── logger
  ├── event_service ◄── system_events
  ├── tag_registry
  ├── tag_runtime ◄── tag_registry
  ├── core ◄── tag_runtime, protocol_dispatcher, event_service
  ├── modbus_service ◄── modbus_codec, tag_registry, acquisition
  ├── protocol_dispatcher ◄── modbus_service, system_service
  ├── acquisition ◄── tag_registry, tag_runtime, protocol_dispatcher
  ├── wifi_service ◄── event_service
  ├── mqtt_service ◄── subscriber, event_service
  ├── publisher ◄── tag_runtime, mqtt_service
  ├── subscriber ◄── tag_registry, protocol_dispatcher, core, mqtt_service
  └── alert_service ◄── event_service, mqtt_service

# 8. Initialization Sequence

The system boots in strict dependency order:

| Step | Call | Purpose |
| --- | --- | --- |
| 1 | logger_init() | Serial @ 115200 baud |
| 2 | event_init() | ESP-IDF default event loop |
| 3 | Register app_event_handler | Lifecycle coordination |
| 4 | alert_init() | Alert queue & event subscriptions |
| 5 | tag_runtime_init() | Allocate runtime array for 8 tags |
| 6 | core_init() | State machine initialization |
| 7 | modbus_init() | Serial1 @ 19200 baud, 8N2 |
| 8 | protocol_dispatcher_init() | Request queue |
| 9 | acquisition_init() | Response queue (30 slots) |
| 10 | publisher_init() | Publish interval config |
| 11 | subscriber_init() | Subscriber queue |
| 12 | wifi_init() | WiFi STA mode config |
| 13 | mqtt_init() | Broker URI, credentials, LWT |
| 14 | alert_start() | Alert processing task |
| 15 | core_start() | State machine task (2s eval) |
| 16 | protocol_dispatcher_start() | Dispatcher task |
| 17 | acquisition_start() | Scan task (10s interval,) |
| 18 | wifi_start() | WiFi FSM task → connects |
| 19 | NETWORK_UP → mqtt_start() | MQTT connection attempt (event-driven) |
| 20 | MQTT_CONNECTED → publisher + subscriber start | Telemetry & command processing (event-driven) |

# 9. Configuration Summary

| Parameter | Value |
| --- | --- |
| WiFi | STA mode, auto-reconnect 20s |
| MQTT Broker | www.hostname.com:1883 |
| MQTT Keep-Alive | 120 seconds |
| MQTT Clean Session | false |
| MQTT LWT Topic | ECO/WS-1/MQTT-STATUS |
| Modbus Baud Rate | Configurable (for my demo: 19200 (8N2)) |
| Modbus TX/RX Pins | Configurable (for my demo: GPIO 17 / GPIO 18) |
| Modbus Timeout | 2000 ms |
| Acquisition Scan Interval | 10,000 ms |
| Publisher Interval | 20,000 ms |
| Core Evaluation Period | 2,000 ms |
| Pressure Fault Threshold | < 20 psi |
| Salt Fault Threshold | < 10% |
| Regen Timeout | 120,000 ms (2 min) |

# 10. File Structure

EcoWell_MQTT-MODBUS_GATEWAY/
├── platformio.ini              # Build config — ESP32-S3, libs, flags
├── include/                    # Header files (public interfaces)
│   ├── system_err.h            # Universal error codes
│   ├── logger.h                # Logging macros & functions
│   ├── event_service.h         # Event bus API
│   ├── system_events.h         # Event ID definitions
│   ├── tag_registry.h          # Tag config structs & enums
│   ├── tag_runtime.h           # Runtime value cache
│   ├── modbus_codec.h          # Register encode/decode
│   ├── modbus_service.h        # Modbus RTU master
│   ├── protocol_dispatcher.h   # Protocol routing
│   ├── system_service.h        # System tag reader
│   ├── acquisition.h           # Scan engine
│   ├── mqtt_service.h          # MQTT client
│   ├── publisher.h             # MQTT publisher
│   ├── subscriber.h            # MQTT subscriber
│   ├── core.h                  # Business logic state machine
│   ├── alert_service.h         # Alert generation
│   └── wifi_service.h          # WiFi manager
├── src/                        # Implementation files
│   ├── main.cpp                # Entry point & orchestrator
│   ├── logger.cpp              # Thread-safe serial logging
│   ├── event_service.cpp       # ESP event loop wrapper
│   ├── system_events.cpp       # Event base definitions
│   ├── tag_registry.cpp        # 8 tag definitions
│   ├── tag_runtime.cpp         # Runtime value store
│   ├── modbus_codec.cpp        # Data type codec
│   ├── modbus_service.cpp      # Modbus RTU driver
│   ├── protocol_dispatcher.cpp # Request router
│   ├── system_service.cpp      # System tag handler
│   ├── acquisition.cpp         # Cyclic scan task
│   ├── mqtt_service.cpp        # MQTT client lifecycle
│   ├── publisher.cpp           # Telemetry publisher
│   ├── subscriber.cpp          # Command subscriber
│   ├── core.cpp                # Water softener FSM
│   ├── alert_service.cpp       # Event-to-alert translator
│   └── wifi_service.cpp        # WiFi connection FSM
├── lib/                        # Local libraries (empty)
└── test/                       # Unit tests (empty)

# 11. Enum Ranges

Each module uses a unique hundred-block for its enum values to prevent collisions:

| Range | Module |
| --- | --- |
| 10–13 | Word order (tag_registry) |
| 20–22 | Tag access mode |
| 30–32 | Tag source |
| 40–41 | Tag topic type |
| 50–56 | Tag data type |
| 100–104 | Log levels (logger) |
| 150–154 | WiFi connection state |
| 200–203 | WiFi service state / Protocol dispatcher state |
| 300–303 | Acquisition state |
| 400–406 | Core state / App events |
| 500–503 | Publisher state |
| 600–603 | Subscriber state |
| 610–614 | MQTT state |
| 700–705 | Core events |

# 12. Summary

This project demonstrates a production-quality embedded IoT gateway architecture with:

Clean layered design — Foundation → Data Model → Protocol → Connectivity → Application

Event-driven architecture — Modules communicate via events, not direct coupling

Real-time concurrency — 8 FreeRTOS tasks with queues, mutexes, and spinlocks

Protocol abstraction — The dispatcher pattern allows adding CAN or other protocols without touching the acquisition engine

Robust lifecycle management — Every service follows init → start → stop with state validation

Fault tolerance — Auto-reconnect for WiFi and MQTT, Modbus health tracking, watchdog fault handler

Domain intelligence — A state machine encodes water softener business rules (fault detection, regeneration management)

Total codebase: ~2,400 lines of C++ across 17 modules, with zero external framework dependencies beyond Arduino, FreeRTOS (built-in), and three well-chosen libraries (eModbus, PsychicMqttClient, ArduinoJson).